THE SEWER BOARD MEETING OF THE CIVIL CITY OF NEW ALBANY, INDIANA, WAS HELD IN THE THIRD FLOOR ASSEMBLY ROOM OF THE CITY-COUNTY BUILDING ON THURSDAY, FEBRUARY 13, 2020 AT 9:15 A.M.

PRESENT: Ed Wilkinson, member, Nathan Grimes, member and Mayor Gahan.

ALSO PRESENT:  April Dickey, Linda Moeller, Rob Sartell, Shane Gibson, Wes Christmas, Larry Summers and Vicki Glotzbach

CALL TO ORDER:

Mayor Gahan called the meeting to order at 9:15 a.m.

PLEDGE OF ALLEGIANCE:

APPROVAL OR CORRECTION OF THE FOLLOWING MINUTES:

Mr. Grimes moved to approve the January 23, 2020 Regular Meeting Minutes, Mr. Wilkinson second, all voted in favor.

BIDS/CONTRACTS:

1.  Rob Sartell re: Change Order for EZ Construction Co., Inc.

Mr. Sartell stated that he has a change order for the phosphorus removal system project and explained that they had to extend the feedline to the chemical feed tank and in doing so, they had to add an outdoor eye wash and shower.  He said the change order is in the amount of $35,200.00.

Mr. Grimes stated that it says remote tank fill station.

Mr. Sartell stated that the tank is beside the building but they had to extend the line from the tank to a place that they can actually get the truck to.

Mr. Grimes asked if that is something that we requested them to do.

Mr. Sartell replied yes.

Mr. Grimes moved to approve, Mr. Wilkinson second, all voted in favor.

2.   Rob Sartell re: Quote from Xylem for Flygt equipment for New Albany-               Anderson Park Lift Station

Mr. Sartell stated that this is a quote for two pumps to replace existing pumps at the Anderson Softball Field pump station.  He said this has kind of fallen into a gray area because we thought the parks department was taking care of it and they thought we were taking care of it and it turns out that no one was really taking too good of care of it.  He explained that from the time that station was installed in the 1990s to now, they have adjusted the 100 year flood levels and this station’s control box is going under water when it floods like it has in the last two years.  He said that he is requesting approval for two pumps which will include the control panel and the control panel will actually move above the 100 year flood level when this project takes place.

Mr. Grimes asked if this is just equipment costs.

Mr. Sartell replied yes and stated that installation costs will be added to it.

Mr. Wilkinson asked who will be doing the work.

Mr. Sartell stated that Xylem will be doing it themselves.

Mr. Wilkinson moved to approve, Mr. Grimes second, all voted in favor.

NEW BUSINESS:

- Vitor Bueno re: Sewer Credit Application for The Village at Autumn Grove (Kenzig Road), a sewer credit application for 301 Mt Tabor Road and a sewer credit application for 2239 Charlestown Road. 502-779-0039

Mr. Brinkworth stated that he is representing Mr. Bueno on his project off of Kenzig Road.  He explained that they are adding 15 lots in the subdivision and he has designed a sewer line to go from Autumn Grove Circle over to the project site and then tie it in.

Mr. Grimes asked if it has already been to plan commission for approval.

Mr. Brinkworth replied yes.

Mr. Grimes asked Mr. Sartell where that will put us credit wise.

Mr. Sartell stated that at the end of the day if everything is approved here today, it will bring our total down to 19,100 but we have 380,000 pending from the EPA.

Mr. Wilkinson asked if we have had any communication on those additional 380,000 credits.

Mr. Christmas stated that he has received a response from the EPA and they have asked for additional information and he is in the process of compiling that right now.  He said that they want a lot of details on the new projects that have been completed and some data showing that they have been effective.  He said that in his opinion, based on the Consent Decree and the language, we are due those credits.

Mr. Wilkinson stated that we have enough discussions with new projects to blow that 380,000 halfway.

Mr. Christmas stated that in addition to the request for those credits we have also requested for the demonstration period to begin as well to just eliminate that.

Mr. Wilkinson asked if we are in any jeopardy of any penalty because we are getting the cart ahead of the horse.

Mr. Christmas stated that he doesn’t think so because we do still have a credit balance remaining, plus he thinks that we should get a fairly prompt response especially on the credit request once we supply the additional information.  He added that the demonstration period is probably just a little more complicated.

Mr. Grimes moved to approve the sewer credits for 4650 gallons per day for the Village at Autumn Grove LLP, Mr. Wilkinson second, all voted in favor.

Mr. Bueno stated that they also have a project at 2239 Charlestown Road where they are building a 24 unit apartment building.

Mr. Sartell stated that would be for 6,000 credits.

Mr. Grimes asked if that is for Max Real Estate.

Mr. Bueno replied yes.

Mr. Grimes moved to approve 6,000 sewer credits for Max Real Estate for a 24 unit apartment building at 2239 Charlestown Road, Mr. Wilkinson second, all voted in favor.

Mr. Bueno stated that the third project is on Mt. Tabor Road and Progress Boulevard where they are building a 9,000 sq. ft. office building.

Mr. Summers asked if he is making a request for a possible build out of that.  He said that the credits would depend on the configuration of how many offices are in there.

Mr. Sartell stated that it is calculated for 35 total employees.

Mr. Grimes stated that it is 700 sewer credits.

Mr. Grimes moved to approve 700 sewer credits for the office building at 301 Mt. Tabor Road, Mr. Wilkinson second, all voted in favor.

- Steve Triplett, Allterrain Paving & Construction re: Oak Street emergency sewer repair

Mr. Triplett stated that the bid was not to exceed $389,032.58.  He said his internal costs went over about $4,000.00 or $5,000.00 but he went ahead and honored the not to exceed price.  He stated the pipe bursting had a small change order in the amount of $15,750.00.  He said that the third line was bypass pumping and he did make a note at the time of bidding that he was going to charge $2,500.00 for additional pumping which covers the two pumps and the fuel but did lower that to $1,656.00 per day.  He explained that the bypass pumping was to be until November 18th but ran over 22 days so he is asking for $36,432.00.

Mr. Wilkinson asked if Mr. Christmas and Mr. Sartell were involved in the discussion on the $15,750.00 for the pipe bursting.

Mr. Christmas replies yes and stated that it was additional costs from the original scope which was to slip line those segments but due to the condition and blockages, it was determined the slip lining was not going to be effective so they had to change to pipe bursting.  He said that pipe bursting added additional costs because additional pits were excavated for that method that weren’t going to be necessary for the slip lining approach so that is where the bulk of that extra cost came from.

Mr. Wilkinson stated that the $389,032.58 not to exceed and our hiring of Clark Dietz to provide additional assistance in the project was extra costs for us.  He said that the approval of the $15,750.00 by Clark Dietz he can go along with but the $36,432.00 is inside the $389,032.58.

Mr. Triplett said he stated it in his bid that the price he was giving of $389,032.58 was to that date.

Mayor Gahan asked Mr. Christmas if that was the way it was.  He said that the board is looking for some guidance.

Mr. Sartell stated that the $36,432.00 was outside of the numbers they were dealing with.

Mr. Triplett stated that was a massive bid for him to give a number on and he honored it.  He said that his internal costs went over that but as a good businessman he honored the $389,032.58.

Mr. Christmas requested that the board approve the $15,750.00 on top of the $389,032.58 and then he can follow up with the board to show the documentation that is there just so the board can see everything.

Mayor Gahan said he thinks that makes sense.

Mr. Triplett then passed around his copy of the bid with the note in it about by passing.

Mr. Summers stated that his recommendation to the board would be to approve the $15,750.00 for the pipe bursting and then take the other portion under advisement so that we can look it over and have legal look it over and have a chance to think about it.

Mr. Grimes moved to approve the not to exceed amount of $389,032.58 plus the $15,750.00 for the pipe bursting and to take the $36,432.00 under advisement, Mr. Wilkinson second, all voted in favor.

Mr. Triplett stated that while they were paving Mr. Thompson came out and asked them to connect the cut down by the alley and cut at the intersection of Pearl Street.  He said that he always goes 15 ft. beyond the cut in his bid but Mr. Thompson didn’t want it cobbled up and wanted him to connect the two cuts.  He said that was another 64 ft. X 22 ft. in width and he wanted it milled down 1 ½ inches and paved to make it all one piece.  He said that came to $3,998.72 and he wanted to present that today as well for approval.

Mr. Summers stated that he would take it under advisement but he does know that Mr. Thompson spoke with Mr. Triplett and made the request for additional paving.  He added that it is in conjunction with the policy that we take with all utilities to ensure that we have a better looking product at the final.

Mr. Grimes moved to take this request under advisement, Mr. Wilkinson second, all voted in favor.

- Jason Copperwaite re: Sewer Credits for 309 Spring Street, Form G Companies

Mr. Copperwaite stated that he is present for the rehabilitation of the Centenary Church project and they are wanting to get started in March or April so he is requesting sewer credits for 10,790 gallons per day.

Mr. Wilkinson moved to approve the above request for credits, Mr. Grimes second, all voted in favor.

- Gary Brinkworth re: Sewer credits for project on Lawrence Banet Road

Mr. Brinkworth stated that they have another project they have been working on which consists of 32 lots on Lawrence Banet Road.  He said that it has been through planning and zoning and was approved.  He then requested 9,920 sewer credits.

Mr. Sartell stated that he doesn’t have any requests for sewer credits on this project at all.  He said that he thought he was going to ask permission to connect to our sewer.

Mr. Brinkworth stated that is correct.

Mr. Sartell stated that they never discussed how many credits were needed for this project.

Mr. Grimes asked where we are after that.

Mr. Sartell stated that we would be negative 3,000.

Mayor Gahan asked when the start date is going to be on this project.

Mr. Brinkworth stated it will be in the next month or so but it will take about three years to build out all of the homes.

Mr. Christmas asked Mr. Brinkworth if he would want to request 2/3 of the credits now and come back later for the other 1/3.

Mr. Wilkinson stated that he didn’t want to get ahead of the EPA and just get somebody mad.

Mr. Christmas stated that if he just requested 2/3 that would take us down to zero.

Mr. Summers stated that he would hate to halt all development in the city until we hear back from the EPA.

Mayor Gahan stated that we can’t do that.

Mr. Sartell asked Mr. Brinkworth to send him 1/3 of what he needs and they will approve that which would be about 3,000 and that would leave us with about 6,000.

Mr. Summers stated that he would prefer that this request be taken under advisement so that we can have a couple of weeks until the next meeting to figure out our game plan for the credit allocation for this project.

Mr. Sartell stated that we are only talking two weeks.

Mr. Brinkworth stated that there is a little problem with that because they do want him to finish up and do the final planning.  He said that they would at least have approval of 1/3 knowing that the other 2/3 will be coming.

Mayor Gahan stated that they are going to have to table it and make a phone call and get back to him later in the day.  He also suggested going back and pulling old projects that are outstanding to see if there are any credits just sitting there.

Mr. Sartell stated that there is just one and he has to send them a certified letter letting them know that if they want to move forward they will have to reapply.

Mayor Gahan asked how many that one is.

Mr. Sartell stated 4,600.

Mr. Wilkinson moved to table this request and act on it as soon as they have enough information, Mr. Grimes second, all voted in favor.

COMMUNICATIONS - PUBLIC:

COMMUNICATIONS - CITY OFFICIALS:

SEWER ADJUSTMENTS:

FINANCIAL REPORT:

Mr. Wilkinson stated that the revenue started good for January and we finally got our lien money which will show up in February.  He added that Duke didn’t get their bill in on time so next month we will have two electric bills otherwise all other activity is right on budget.

TABLED ITEMS:

OLD BUSINESS:

1.   Clark Dietz

Mr. Christmas – Silver Hills Project – he stated that Allterrain completed the tying of the force main at the wet well and valve pit and have been working on the internal piping.  He said that they are prepping for the retaining wall that is going to go around where the new wet well sits at the end of the road.  He stated that upcoming activities are finishing out the retaining wall and begin working on electricals and controls at the station.  He then explained that the retaining wall was not a part of the original project but since it is on a hill, they had to build a retaining wall to get a flat area to install the station so there is a change order for approximately $9,000 something.  He said that there was not enough time to get in the packet for this meeting.

Mr. Summers recommended that the board authorize the staff to approve the change order not exceed $10,000.00.

Mr. Wilkinson moved to authorize the staff to approve the change order not to exceed $10,000.00, Mr. Grimes second, all voted in favor.

UTILITY REPORT:

1.   Rob Sartell re: Wastewater Utility Report for November 2019

Influent / Effluent Quality

The treatment plant was in full compliance with the NPDES permit.

Pretreatment

There were 18 grease trap inspections submitted.

An informal Notice of Violation was issued to Huncilman and Son for Nickel monthly maximum exceedance and to Versa Designed Surfaces for TSS daily maximum exceedance.

Facililty Operations

51 dry tons of bio solids were removed from the WWTP.

The WWTP was at 53% of its Total Suspended Solids design limit and at 49% of its CBOD design limit.

There were 3.72 inches of rain for the month

Preventative and Unscheduled Maintenance

178 preventative work orders were completed and 22 corrective work orders were completed for the WWTP and Lift Stations

Highlights

Cleaned wet wells and floats at the following lift stations; Grantline Road, LaFollette and The Pines

The #3 pump at the #110 Raw Wastewater Pump Station air locked. Primed the pump and put it back in service.

Cleaned the gravity belts and sprayer boxes on the #1 and #2 Belt Filter Presses.

Drained and cleaned out the #432 Secondary Clarifier and prepped it for the next wet weather event.

Sanitary Collection System

| Project | Current Month | Year-to-Date |
| --- | --- | --- |
| Sanitary Sewer Flushed/ft | 7,924 | 123,656 |
| Sanitary Sewer Televised/ft. | 6,635 | 123,749 |
| CIPP Installed/ft | 0 | 2,598 |
| Tap Inspections | 9 | 90 |
| Locates | 468 | 8,822 |
| Pipe Patches | 3 | 23 |
| Service Requests | Odor Complaint | Main Block | Resident Problem | Dye Test | Emergency Locates |
| 22 | 0 | 1 | 14 | 0 | 6 |

Sanitary Sewer Overflow Monitoring

There was 1 rain event that required Stantec monitoring and 1 Non-Capacity Related overflow. See air locked pump at #110 RWWPS.

Preventative and Unscheduled Maintenance

24 preventative work orders were completed and 6 corrective work orders were issued for the Collection System.

Construction Highlights

# Manhole Repairs		#Manhole Installations	#Pipe Patches

0				0				1

#Main Line Repairs		#Lateral Repairs		Easement Maintenance

0				0				0

Annual/Semi Annual, Monthly Routine and Preventative Sewer Cleaning

The Line in the alley serving the Exchange, Wick’s Pizza and the Hitching Post.  FOG management.

Completed the annual inspection of 38 collection system Air Relief Valves

Basin #18 – Mills Lane					Basin #16 – Harriet Ct.

Basin #6 – Market St.

Basin #1 – 420ft.		Basin #1A – 1,698ft.		Basin #6 – 644ft.

Basin #18 – 300ft.		Basin #22 – 1,062ft.

Facility Safety

The monthly safety inspection rating was 98.44%

The safety training for the month was on Ladder Safety.

Projects

Reline New Albany

No lining in October

Up Hill Run Lift Station

Preliminary design work is at 90%. Land aquisistion has been achieved.

Wet Weather Clarifier Rehab

Current Progress (1/6/20 – 1/10/20)

 Mitchell and Stark returned to the project this week and worked 2 days on Monday and Tuesday with a 3-man short crew. They grouted around the pressure relief valve in clarifier # 2 and placed several pieces of vertical steel on the new angle truss in the northwest corner of clarifier #2 and welded into place.

Silver Hills Slope Project/Dent Ave. Lift Station

• Monday Jan 6 –No work performed.

• Tuesday Jan 7 –Contractor Mobilized onto jobsite and chose the proposed force main alignment laterally/horizontally, then saw cut and hoe rammed the proposed trench limits.

• Wednesday Jan 8– Contractor began excavation for force main. Contractor had the wrong pipe delivered. Contractor directed to stop laying pipe until the correct type of pipe is delivered. Contractor took off at half day.

• Thursday Jan 9 – Contractor potholed to locate two water services and determined that there is a water main directly in conflict with the proposed trench limits along Highland Ave. These lines had not been located by IAW when the job was initially located and were not shown on the plans. We worked with the contractor to find a suitable location within the pavement for the force main and came up with a solution for them to move forward. There was no loss of time as there was no suitable pipe material on site to install. Contractor took off at half day.

• Friday Jan 10 – Contractor moved over approximately 2.50 ft. toward the centerline from the originally proposed trench sawcut and re-sawed the new trench limit along Highland Ave. Contractor also hoe rammed the newly proposed trench limits to aid with pavement removal.

• Monday 01/13 – APC began to install 4” PVC force main. Installed 180ft.

• Tuesday 01/14 –APC installed 180ft./4”PVC force main.

• Wednesday 01/15– APC installed 180ft./4”PVC force main.

• Thursday 01/16 – APC finished installing 4”PVC force main. Installed 180ft./720ft. to date.

• Friday 01/17 –APC pressure tested the force main. It passed @100p.s.i. for 2 hours.

• Monday 01/20 –APC did trench repair/restore. Concrete poured to the top.

• Tuesday 01/21 –APC did trench repair/restore. Concrete poured to the top.

• Wednesday 01/22 –APC cored and installed the last stick of 4”-PVC force main into the existing manhole at the end project along Highland Ave. APC made the first tie-in to an existing manhole. APC finished the trench restore for what is currently open.

• Thursday 01/23– APC excavated and installed the wet well 1 and valve vault 1 structures for the lift station.

• Friday 01/24 –APC did general clean up and staged ductile iron pipe at the lift station.

• MONDAY 1/27/20 APC sawcut, hoe rammed, excavated the trench, prepped and installed 93l LF of 4” PVC force main. This gets us within “one stick” away from valve vault 1.

• TUESDAY 1/28/20 APC installed ductile iron pipe, and valves into valve vault 1 and wet well 1. CCC (coring subcontractor) cored valve vault 1 for outlet. Placement was wrong. Will need re-cored.

• WEDNESDAY 1/29/20 APC installed ductile iron pipe, and valves into valve vault 1 and wet well 1.

• THURSDAY 1/30/20 No work performed by APC, as half the crew called in.

• FRIDAY 1/31/20 APC installed ductile iron pipe and valve to valve vault 1 and wet well 1.

CLAIMS:

Mrs. Moeller presented the following claims for the period of 01/23/20 to 02/12/20 in the amount of $1,592,047.33 which does not include the $36,432.00 for Allterrain that was tabled earlier in the meeting:

| Sewer Claims | Amount | Dept. |
| --- | --- | --- |
| OFFICE SUPPLY COMPANY, INC | 100.30 | SEW |
| OFFICE SUPPLY COMPANY, INC | 31.95 | SEW |
| OFFICE SUPPLY COMPANY, INC | 59.30 | SEW |
| L&D MAILMASTERS, INC. | 1,371.92 | SEW |
| L&D MAILMASTERS, INC. | 223.30 | SEW |
| L&D MAILMASTERS, INC. | 2,496.50 | SEW |
| CK REAL ESTATE LLC | 2,979.16 | SEW |
| CK REAL ESTATE LLC | 541.66 | SEW |
| PARIS, MARIA | 151.20 | SEW |
| BELLO PROPERTIES, LLC. | 139.79 | SEW |
| BELLO PROPERTIES, LLC. | 114.56 | SEW |
| SERENITY PRIMARY CARE | 30.72 | SEW |
| MARSHALL, ASHLEY | 97.52 | SEW |
| BIRGE, SARAH | 148.74 | SEW |
| Total | 8,486.62 |  |
| ACE HARDWARE | 37.98 | WWTP |
| ACE HARDWARE | 81.48 | WWTP |
| ACE HARDWARE | 19.99 | WWTP |
| ACE HARDWARE | 40.96 | WWTP |
| ACE HARDWARE | 13.99 | WWTP |
| ACE HARDWARE | 11.56 | WWTP |
| ACE HARDWARE | 12.99 | WWTP |
| ACE HARDWARE | 14.97 | WWTP |
| ACE HARDWARE | 10.99 | WWTP |
| ACE HARDWARE | 31.96 | WWTP |
| ACE HARDWARE | 26.96 | WWTP |
| ACE HARDWARE | 50.91 | WWTP |
| ACE HARDWARE | 19.94 | WWTP |
| ACE HARDWARE | 17.98 | WWTP |
| ACE HARDWARE | 104.57 | WWTP |
| ACE HARDWARE | 29.76 | WWTP |
| ACE HARDWARE | 16.89 | WWTP |
| PLUMBERS SUPPLY | 13.48 | WWTP |
| PLUMBERS SUPPLY | 18.43 | WWTP |
| KLEIN BROTHERS SAFE & LOCK | 782.36 | WWTP |
| BLACK DIAMOND | 65.00 | WWTP |
| BLACK DIAMOND | 45.00 | WWTP |
| MURPHY ELEVATOR COMPANY, INC. | 163.55 | WWTP |
| QUILL | 112.44 | WWTP |
| QUILL | 93.96 | WWTP |
| QUILL | 176.62 | WWTP |
| QUILL | 51.99 | WWTP |
| QUILL | 821.92 | WWTP |
| QUILL | 46.98 | WWTP |
| CINTAS #302 | 69.76 | WWTP |
| CINTAS #302 | 84.76 | WWTP |
| CLARK-DIETZ | 43,644.01 | WWTP |
| CLARK-DIETZ | 14,078.73 | WWTP |
| AAA PLUBMING LLC. | 389.00 | WWTP |
| ORR SAFETY EQUIPMENT CO. | 1,350.00 | WWTP |
| ORR SAFETY EQUIPMENT CO. | 340.00 | WWTP |
| ORR SAFETY EQUIPMENT CO. | 1,890.00 | WWTP |
| EARTH FIRST | 345.87 | WWTP |
| J.R. HOE & SONS INC. | 145.00 | WWTP |
| ALLIED TECHNICAL SVCS, INC | 6,972.40 | WWTP |
| IN DEPT OF ENVIRONMENTAL MGMT | 16,500.00 | WWTP |
| DELTA SERVICES, LLC | 1,893.17 | WWTP |
| RODEFER MOSS & CO., PLLC | 1,375.00 | WWTP |
| SPENCER MACHINE & TOOL CO.,INC | 581.25 | WWTP |
| SPENCER MACHINE & TOOL CO.,INC | 1,788.70 | WWTP |
| SPENCER MACHINE & TOOL CO.,INC | 1,056.39 | WWTP |
| STANTEC CONSULTING SERVICES | 2,158.75 | WWTP |
| GRIPP, INC. | 4,289.67 | WWTP |
| GRIPP, INC. | 4,289.67 | WWTP |
| GRIPP, INC. | 4,289.67 | WWTP |
| GRIPP, INC. | 6,421.67 | WWTP |
| OFFICE DEPOT | 97.38 | WWTP |
| HOME DEPOT | 17.98 | WWTP |
| HOME DEPOT | 58.91 | WWTP |
| HOME DEPOT | 79.80 | WWTP |
| AIRGAS-MID AMERICA | 199.13 | WWTP |
| PRO4MANCE CONTRACTING SERVICES | 4,281.44 | WWTP |
| PRO4MANCE CONTRACTING SERVICES | 2,017.30 | WWTP |
| PRO4MANCE CONTRACTING SERVICES | 756.63 | WWTP |
| PRO4MANCE CONTRACTING SERVICES | 435.20 | WWTP |
| QUARTZ LAMPS INC | 9,800.00 | WWTP |
| RIVER CITY WORK WEAR | 235.00 | WWTP |
| RIVER CITY WORK WEAR | 127.96 | WWTP |
| RIVER CITY WORK WEAR | 309.90 | WWTP |
| HACH COMPANY | 787.77 | WWTP |
| ENVIRONMENTAL LABORATORIES INC | 30.00 | WWTP |
| ENVIRONMENTAL RESOURCE ASSOCIA | 815.86 | WWTP |
| IDEXX DISTRIBUTION, INC | 3,701.67 | WWTP |
| IDEXX DISTRIBUTION, INC | 750.00 | WWTP |
| SARTELL, ROBERT | 55.93 | WWTP |
| SARTELL, ROBERT | 62.88 | WWTP |
| TELEDYNE ISCO | 570.00 | WWTP |
| TELEDYNE ISCO | 246.00 | WWTP |
| IUPPS | 453.15 | WWTP |
| ELEMENT MATERIALS TECHNOLOGY | 23.80 | WWTP |
| ELEMENT MATERIALS TECHNOLOGY | 14.40 | WWTP |
| ELEMENT MATERIALS TECHNOLOGY | 14.40 | WWTP |
| ELEMENT MATERIALS TECHNOLOGY | 23.80 | WWTP |
| ELEMENT MATERIALS TECHNOLOGY | 23.80 | WWTP |
| ELEMENT MATERIALS TECHNOLOGY | 23.80 | WWTP |
| ELEMENT MATERIALS TECHNOLOGY | 14.40 | WWTP |
| ELEMENT MATERIALS TECHNOLOGY | (14.40) | WWTP |
| ELEMENT MATERIALS TECHNOLOGY | (75.80) | WWTP |
| IWEA-INDIANA WATER ENV ASSOC. | 60.00 | WWTP |
| IWEA-INDIANA WATER ENV ASSOC. | 60.00 | WWTP |
| NAPA OF NEW ALBANY | 12.06 | WWTP |
| NAPA OF NEW ALBANY | 24.12 | WWTP |
| NAPA OF NEW ALBANY | 24.12 | WWTP |
| NAPA OF NEW ALBANY | 24.12 | WWTP |
| NAPA OF NEW ALBANY | 311.79 | WWTP |
| NAPA OF NEW ALBANY | 162.69 | WWTP |
| NAPA OF NEW ALBANY | 18.27 | WWTP |
| NAPA OF NEW ALBANY | 964.80 | WWTP |
| NAPA OF NEW ALBANY | 80.22 | WWTP |
| IRTH SOLUTIONS LLC | 3,649.20 | WWTP |
| IRTH SOLUTIONS LLC | 643.35 | WWTP |
| SOURCE 1 ENVIRONMENTAL, LLC | 5,700.00 | WWTP |
| TEAM EJP JEFFERSONVILLE | 631.89 | WWTP |
| GOTTA GO INC. | 729.00 | WWTP |
| GOTTA GO INC. | 972.00 | WWTP |
| GOTTA GO INC. | 1,701.00 | WWTP |
| GOTTA GO INC. | 1,701.00 | WWTP |
| HAYES SHOES | 620.36 | WWTP |
| COVERALL SERVICE COMPANY | 1,075.00 | WWTP |
| ALLTERRAIN PAVING & CONSTRUCT | 404,782.58 | WWTP |
| ALLTERRAIN PAVING & CONSTRUCT | 900.00 | WWTP |
| RILEY, REGINALD | 35.00 | WWTP |
| WATERLOGIC USA INC | 360.00 | WWTP |
| MSC #30157 ENVIRONMENTAL PROD | 128.26 | WWTP |
| BEC ENTERPRISES, LLC | 103.06 | WWTP |
| VALVOLINE, LLC | 91.77 | WWTP |
| GAHL LEGAL GROUP, LLC. | 715.00 | WWTP |
| TENBARGE SEED CO., INC. | 40.00 | WWTP |
| Total | 569,147.83 |  |
| INDIANA AMERICAN WATER | 1,518.65 | TU |
| INDIANA AMERICAN WATER | 40.37 | TU |
| INDIANA AMERICAN WATER | 20.14 | TU |
| INDIANA AMERICAN WATER | 20.14 | TU |
| VERIZON WIRELESS | 2,273.86 | TU |
| VECTREN ENERGY DELIVERY | 156.28 | TU |
| VECTREN ENERGY DELIVERY | 580.23 | TU |
| VECTREN ENERGY DELIVERY | 166.05 | TU |
| VECTREN ENERGY DELIVERY | 1,397.52 | TU |
| VECTREN ENERGY DELIVERY | 175.87 | TU |
| VECTREN ENERGY DELIVERY | 454.86 | TU |
| VECTREN ENERGY DELIVERY | 916.81 | TU |
| AT&T | 554.55 | TU |
| DUKE ENERGY | 29.80 | TU |
| DUKE ENERGY | 260.93 | TU |
| DUKE ENERGY | 657.39 | TU |
| DUKE ENERGY | 255.06 | TU |
| DUKE ENERGY | 20.65 | TU |
| DUKE ENERGY | 42.72 | TU |
| DUKE ENERGY | 22.86 | TU |
| DUKE ENERGY | 778.27 | TU |
| KIMMEL LAWN SERVICE | 3,225.00 | TU |
| KIMMEL LAWN SERVICE | 3,225.00 | TU |
| CROWN SERVICES INC | 1,061.50 | TU |
| CARD SERVICES | 179.20 | TU |
| CARD SERVICES | 964.72 | TU |
| CARD SERVICES | 106.98 | TU |
| NEOPOST | 103.00 | TU |
| SPECTRUM BUSINESS | 1,185.33 | TU |
| MAXIMUM FLEET SERVICE | 465.72 | TU |
| MAXIMUM FLEET SERVICE | 1,540.53 | TU |
| GIBSON LAW OFFICE, LLC | 705.38 | TU |
| GIBSON LAW OFFICE, LLC | 653.40 | TU |
| AT&T | 338.72 | TU |
| L&D MAILMASTERS, INC. | 753.61 | TU |
| L&D MAILMASTERS, INC. | 221.96 | TU |
| CROWN SERVICES INC | 1,217.50 | TU |
| AT&T | 98.91 | TU |
| VERIZON CONNECT MWF, INC. | 265.00 | TU |
| INDIANA AMERICAN WATER | 40.37 | TU |
| INDIANA AMERICAN WATER | 42.38 | TU |
| INDIANA AMERICAN WATER | 40.37 | TU |
| INDIANA AMERICAN WATER | 42.83 | TU |
| INDIANA AMERICAN WATER | 20.14 | TU |
| INDIANA AMERICAN WATER | 20.14 | TU |
| INDIANA AMERICAN WATER | 40.86 | TU |
| INDIANA AMERICAN WATER | 40.37 | TU |
| INDIANA AMERICAN WATER | 250.63 | TU |
| NEW ALBANY MUNICIPAL UTILTIES | 4.17 | TU |
| NEW ALBANY MUNICIPAL UTILTIES | 4.17 | TU |
| NEW ALBANY MUNICIPAL UTILTIES | 4.17 | TU |
| NEW ALBANY MUNICIPAL UTILTIES | 4.17 | TU |
| STORMWATER\DRAINAGE FUND | 352,992.48 | TU |
| SANITATION FUND | 191,973.32 | TU |
| BANK OF NEW YORK TRUST CO. | 460,996.00 | TU |
| FLOYDS KNOBS WATER | 24.36 | TU |
| FLOYDS KNOBS WATER | 24.36 | TU |
| FLOYDS KNOBS WATER | 26.07 | TU |
| AT&T | 67.24 | TU |
| DUKE ENERGY | 4,538.43 | TU |
| DUKE ENERGY | 72.85 | TU |
| DUKE ENERGY | 800.91 | TU |
| DUKE ENERGY | 663.58 | TU |
| DUKE ENERGY | 251.66 | TU |
| DUKE ENERGY | 1,503.00 | TU |
| DUKE ENERGY | 176.39 | TU |
| DUKE ENERGY | 1,422.46 | TU |
| DUKE ENERGY | 76.50 | TU |
| DUKE ENERGY | 1,053.86 | TU |
| CROWN SERVICES INC | 984.00 | TU |
| WEX BANK | 5,227.32 | TU |
| SPECTRUM BUSINESS | 23.12 | TU |
| KETTLER, JOHN | 99.18 | TU |
| GIBSON LAW OFFICE, LLC | 638.55 | TU |
| Total | 1,050,844.88 |  |
| Grand Total | 1,628,479.33 |  |

Amended Grand Total      1,592,047.33

Mr. Grimes moved to approve the above claims as amended, Mr. Wilkinson second, all voted in favor.

ADJOURN:

There being no further business before the board, the meeting adjourned at 9:58 a.m.

_____________________________			____________________________

Mayor Gahan, President				Vicki Glotzbach, City Clerk