THE SEWER BOARD MEETING OF THE CIVIL CITY OF NEW ALBANY, INDIANA, WILL BE HELD VIA ZOOM.COM ON THURSDAY, FEBRUARY 11, 2021 AT 9:15 A.M.

PRESENT: Ed Wilkinson, member, Nathan Grimes, member and Mayor Gahan, President. 

ALSO PRESENT:  April Dickey, Linda Moeller, Wes Christmas, Rob Sartell, and Vicki Glotzbach

CALL TO ORDER:

Mayor Gahan called the meeting to order at 9:15 a.m.

PLEDGE OF ALLEGIANCE:

APPROVAL OR CORRECTION OF THE FOLLOWING MINUTES:

Mr. Grimes moved to approve the January 28, 2021 Regular Meeting Minutes, Mr. Wilkinson second, all voted in favor.

BIDS/CONTRACTS:

NEW BUSINESS:

COMMUNICATIONS - PUBLIC:

COMMUNICATIONS - CITY OFFICIALS:

SEWER ADJUSTMENTS:

FINANCIAL REPORT:

Mr. Wilkinson stated that as mentioned the revenue last month was a little short but they did make it up. He reported that income was $1.5M, which includes the $127,000.00 of lien money that was recorded so they are back to operating inside of the budget.

TABLED ITEMS:

OLD BUSINESS:

1. Clark Dietz

Mr. Christmas – Silver Hills Lift Station – he reported that the contractor attempted another start-up and found that the pumps weren’t outputting exactly what they should have been based on the design. He stated that they have asked the contractor to do some additional troubleshooting to resolve this issue, so the station is running but it is running at a slightly reduced output. He added that they still need to compete the outstanding landscaping and other weather related items. Basin 13 – he reported that they are ready to advertise and will proceed as discussed at the last meeting.

Mayor Gahan asked if he has any ideas of what the issue could be at Silver Hills.

Mr. Christmas explained that there are always a lot of unknown factors with pumping systems that could influence the output. He stated that they went through a lot of these factors to try to determine where the issues. He added that the manufacture is going to be replacing the pumps to see if it is an issue with them not performing as they should. He explained that the reduced output is not going to cause an issue but they are going to keep troubleshooting until it is performing closer to what it should be.

UTILITY REPORT:

New Albany Wastewater Utility Monthly Report Summary for November 2020

Mr. Sartell reported on the following:

Influent / Effluent Quality
The treatment plant was in full compliance with the NPDES permit.

Pretreatment
There were 10 grease trap inspections submitted.
Annual sampling took place at the following permitted dischargers; Bruce Fox and K&I Hardchrome.

Facililty Operations
52 dry tons of bio solids were removed from the WWTP.
The WWTP was at 63% of its Total Suspended Solids design limit and at 47% of its CBOD design limit.  
There were 2.56 inches of rain for the month

Preventative and Unscheduled Maintenance
212 preventative work orders were completed and 14 corrective work orders were completed for the WWTP and Lift Stations

Highlights
Replaced VFD fans and a blown relay at Wolf Lake Lift Station. 
Replaced the VFD on the #9 Return Activated Sludge pump. 
Replaced the Gear Box on the #5 Secondary Clarifier drive.   
Cleaned Wet Well at The Pines, Quarry Road, Wolf Lake, Prosser and McLean Lift Stations. 
Topped off fuel tanks for the generators at Prosser, LaFollette and Mt. Tabor Lift Stations.

Sanitary Collection System

| Project | Current Month | Year-to-Date |
| --- | --- | --- |
| Sanitary Sewer Flushed/ft | 6,837 | 77,846 |
| Sanitary Sewer Televised/ft. | 6,998 | 60,169 |
| CIPP Installed/ft | 0 | 0 |
| Tap Inspections | 5 | 84 |
| Locates | 1,129 | 8,694 |
| Pipe Patches | 1 | 9 |
| Service Requests | Odor Complaint | Main Block | Resident Problem | Dye Test | Emergency Locates |
| 14 | 1 | 1 | 8 | 0 | 5 |

Sanitary Sewer Overflow Monitoring
There were 0 rain events that required Stantec monitoring. There were no overflows reported.

Preventative and Unscheduled Maintenance
23 preventative work orders were completed and 4 corrective work orders were issued for the Collection System.

Construction Highlights

# Manhole Repairs		#Manhole Installations	#Pipe Patches

0				0				1

#Main Line Repairs		#Lateral Repairs		Easement Maintenance

0				1				0

Annual/Semi Annual, Monthly Routine and Preventative Sewer Cleaning
The Line in the alley serving the Exchange, Parlour Pizza and the Hitching Post.  FOG management.

Scheduled Preventative Maintenance
Basin #2 – Spring Ave.			Basin #16 – Oriole Dr.

Monthly Routine Cleaning and CCTV							
Basin #1A – 540	ft.	Basin #2 – 205ft.	Basin #4 – 2,697ft.	Basin #20 – 227ft
Basin #21 – 329ft.

Facility Safety
The monthly safety inspection rating was 99.22%. Safety training covered Arc Flash.

Projects

Reline New Albany
No lining in September

Up Hill Run Lift Station
Preliminary design work is at 90%. Land aquisistion has been achieved

Silver Hills Slope Project/Dent Ave. Lift Station

- WEDNESDAY 11/18/20

Lift station startup meeting.  Flow is connected to wet well of lift station and existing gravity line has been connected to new gravity line.  Using the available sewage in the wet well we were able to verify that the system was getting power and that both pumps ran.  There was not enough sewage to continue testing the system, and the contractor did not have a water meter and hose for the hydrant to refill the wet well.  A second startup meeting was scheduled between the contractor and the inspector for ultimately 12/1/20.

It was brought to our attention that the provision for a water service and self-draining spigot was not included in the design.

The SCADA technician arrived and tested the system manually to ensure that the alarms were being delivered to the computers at the treatment plant.  In the process we found out that the “PLC Fault” alarm had not yet been installed.  The technician was able to do the installation from the field and we were able to verify that this alarm was communicating with the treatment plant.  No other issues were encountered with the SCADA system.

CLAIMS:

Mrs. Moeller presented the following claims for the period of 01/21/20 to 02/03/21 in the amount of $191,708.06:

| Sewer Claims | Amount | Dept |
| --- | --- | --- |
| BORDEN TRI-COUNTY WATER | 340.20 | SEW |
| L&D MAILMASTERS, INC. | 1,381.11 | SEW |
| L&D MAILMASTERS, INC. | 226.46 | SEW |
| CROWN SERVICES INC | 1,240.00 | SEW |
| BELCHER, LAURA | 129.68 | SEW |
| Total | 3,317.45 |  |
| GIBSON LAW OFFICE, LLC | 549.45 | WWTP |
| ACE HARDWARE | 12.45 | WWTP |
| ACE HARDWARE | 2.69 | WWTP |
| ACE HARDWARE | 43.93 | WWTP |
| ACE HARDWARE | 10.76 | WWTP |
| ACE HARDWARE | 29.98 | WWTP |
| ACE HARDWARE | 44.36 | WWTP |
| ACE HARDWARE | 4.98 | WWTP |
| ACE HARDWARE | 43.98 | WWTP |
| ACE HARDWARE | 10.98 | WWTP |
| ACE HARDWARE | 7.99 | WWTP |
| ACE HARDWARE | 7.99 | WWTP |
| ACE HARDWARE | 24.99 | WWTP |
| ACE HARDWARE | 95.99 | WWTP |
| ACE HARDWARE | 40.96 | WWTP |
| BLACK DIAMOND | 65.00 | WWTP |
| BLACK DIAMOND | 45.00 | WWTP |
| CLARK-FLOYD LANDFILL LLC. | 9,602.55 | WWTP |
| BIG O TIRES | 20.00 | WWTP |
| QUILL | 5.79 | WWTP |
| QUILL | 139.49 | WWTP |
| QUILL | 763.18 | WWTP |
| QUILL | 319.57 | WWTP |
| QUILL | 39.99 | WWTP |
| QUILL | 44.37 | WWTP |
| QUILL | 241.41 | WWTP |
| QUILL | 18.99 | WWTP |
| QUILL | 37.18 | WWTP |
| CINTAS #302 | 84.76 | WWTP |
| CINTAS #302 | 84.76 | WWTP |
| CLARK-DIETZ | 7,993.92 | WWTP |
| BYRNE'S GARAGE INC. | 245.55 | WWTP |
| IN DEPT OF ENVIRONMENTAL MGMT | 14,500.00 | WWTP |
| BIOCHEM, INC. | 10,196.16 | WWTP |
| DELTA SERVICES, LLC | 1,579.32 | WWTP |
| DELTA SERVICES, LLC | 192.00 | WWTP |
| EYE-TRONICS | 861.25 | WWTP |
| EYE-TRONICS | 525.65 | WWTP |
| HOME DEPOT | 398.00 | WWTP |
| HOME DEPOT | 179.00 | WWTP |
| HOME DEPOT | 299.00 | WWTP |
| HOME DEPOT | 20.00 | WWTP |
| HOME DEPOT | 19.98 | WWTP |
| AIRGAS-MID AMERICA | 163.80 | WWTP |
| PRO4MANCE CONTRACTING SERVICES | 5,508.34 | WWTP |
| RABEN TIRE CO. | 23.07 | WWTP |
| INDEPENDENT PIPING, INC. | 4,166.95 | WWTP |
| RIVER CITY WORK WEAR | 88.00 | WWTP |
| HACH COMPANY | 361.17 | WWTP |
| WALKER PROCESS EQUIPMENT | 161.19 | WWTP |
| IUPPS | 587.10 | WWTP |
| APPLEGATE FIFER PULLIAM-WIRE | 1,105.50 | WWTP |
| APPLEGATE FIFER PULLIAM-WIRE | 379.50 | WWTP |
| ELEMENT MATERIALS TECHNOLOGY | 23.80 | WWTP |
| IWEA-INDIANA WATER ENV ASSOC. | 35.00 | WWTP |
| NAPA OF NEW ALBANY | 13.98 | WWTP |
| NAPA OF NEW ALBANY | 11.49 | WWTP |
| NAPA OF NEW ALBANY | 394.33 | WWTP |
| NAPA OF NEW ALBANY | 6.94 | WWTP |
| IRTH SOLUTIONS LLC | 3,758.68 | WWTP |
| GOTTA GO INC. | 1,068.00 | WWTP |
| ALLTERRAIN PAVING & CONSTRUCT | 395.00 | WWTP |
| DISCOVERY BUILDERS | 6,100.00 | WWTP |
| VERIZON CONNECT MWF, INC. | 253.66 | WWTP |
| VALVOLINE, LLC | 106.22 | WWTP |
| VALVOLINE, LLC | 93.47 | WWTP |
| VALVOLINE, LLC | 106.22 | WWTP |
| BMV ELECTRIC COMPANY, LLC. | 8,800.00 | WWTP |
| DEMING,MALONE,LIVESAY & OSTROF | 1,400.00 | WWTP |
| Total | 84,564.76 |  |
| SILVER CREEK WATER | 2,662.00 | TU |
| SILVER CREEK WATER | 17.03 | TU |
| SILVER CREEK WATER | 17.03 | TU |
| SILVER CREEK WATER | 17.03 | TU |
| SILVER CREEK WATER | 15.40 | TU |
| SILVER CREEK WATER | 17.03 | TU |
| SILVER CREEK WATER | 17.03 | TU |
| SILVER CREEK WATER | 17.03 | TU |
| SILVER CREEK WATER | 17.03 | TU |
| VERIZON WIRELESS | 2,326.24 | TU |
| HARRISON CO. REMC | 458.18 | TU |
| HARRISON CO. REMC | 104.13 | TU |
| HARRISON CO. REMC | 43.98 | TU |
| VECTREN ENERGY DELIVERY | 523.26 | TU |
| VECTREN ENERGY DELIVERY | 146.46 | TU |
| VECTREN ENERGY DELIVERY | 1,026.02 | TU |
| VECTREN ENERGY DELIVERY | 144.05 | TU |
| VECTREN ENERGY DELIVERY | 440.91 | TU |
| VECTREN ENERGY DELIVERY | 1,035.06 | TU |
| FLOYDS KNOBS WATER | 7,790.10 | TU |
| FLOYDS KNOBS WATER | 111.98 | TU |
| EDWARDSVILLE WATER CO. | 17.00 | TU |
| DUKE ENERGY | 376.43 | TU |
| DUKE ENERGY | 60,047.63 | TU |
| DUKE ENERGY | 785.71 | TU |
| DUKE ENERGY | 349.53 | TU |
| DUKE ENERGY | 31.08 | TU |
| DUKE ENERGY | 821.80 | TU |
| CARD SERVICES | 834.40 | TU |
| CARD SERVICES | 119.55 | TU |
| CARD SERVICES | 48.12 | TU |
| CARD SERVICES | 192.48 | TU |
| CARD SERVICES | 110.76 | TU |
| SPECTRUM BUSINESS | 724.90 | TU |
| SPECTRUM BUSINESS | 128.29 | TU |
| GAHL LEGAL GROUP, LLC. | 1,760.00 | TU |
| GIBSON LAW OFFICE, LLC | 564.30 | TU |
| INDIANA AMERICAN WATER | 693.33 | TU |
| INDIANA AMERICAN WATER | 39.99 | TU |
| INDIANA AMERICAN WATER | 41.93 | TU |
| INDIANA AMERICAN WATER | 19.89 | TU |
| INDIANA AMERICAN WATER | 19.89 | TU |
| GIBSON LAW OFFICE, LLC | 594.00 | TU |
| CLARK CO. REMC | 138.42 | TU |
| CLARK CO. REMC | 218.24 | TU |
| CLARK CO. REMC | 370.53 | TU |
| CLARK CO. REMC | 157.09 | TU |
| CLARK CO. REMC | 149.77 | TU |
| HENRY P. THOMPSON CO. | 15,795.72 | TU |
| AT&T | 552.27 | TU |
| DUKE ENERGY | 337.23 | TU |
| DUKE ENERGY | 21.41 | TU |
| DUKE ENERGY | 46.10 | TU |
| DUKE ENERGY | 25.42 | TU |
| QUADIENT FINANCE USA, INC. | 26.00 | TU |
| CONSTELLATION NEWENERGY | 719.66 | TU |
| Total | 103,825.85 |  |
| Grand Total | 191,708.06 |  |

Mr. Wilkinson moved to approve, Mr. Grimes second, all voted in favor

ADJOURN:

Mayor Gahan stated that there is more bad weather coming in over the next couple of days and asked everyone to be extra cautious.

There being no further business before the board, the meeting adjourned at 9:11 a.m.

_____________________________			____________________________

Mayor Gahan, President				Vicki Glotzbach, City Clerk